## Sheet0
Installed power
Boilers thermal power (kW) | 8046.5173
Pellet boilers thermal power (kW) | 0
CHPs thermal power (kW) | 72.4527
HPs condenser thermal power (kW) | 1934.833
Gas absorption HPs thermal power (kW) | 0
Solar collectors thermal power (kW) | 50
HP/Chillers condenser thermal power (kW) | 1518
HP/Chillers evaporator thermal power (kW) | 1180
Chillers evaporator thermal power (kW) | 3295
Cooling towers thermal power (kW) | 150
Total installed power heating (kW) | 11621.803
Total installed power cooling (kW) | 4625
Installed power contribution
Boilers power contribution (%) | 69.24%
Pellet boilers power contribution (%) | 0%
CHPs power contribution (%) | 0.6234%
HPs condenser power contribution (%) | 16.65%
Gas absorption HPs power contribution (%) | 0%
Solar collectors power contribution (%) | 0.4302%
HP/Chillers condenser power contribution (%) | 13.06%
HP/Chillers evaporator power contribution (%) | 25.51%
Chillers evaporator power contribution (%) | 71.24%
Cooling towers power contribution (%) | 3.243%
Heating system
Building load central heating (kWh) | 37775.8812
Building load domestic hot water (kWh)
Pipes thermal losses (kWh) | 120.4077
Thermal energy storage losses (kWh)
Produced heating (kWh) | 27324.2552
Cooling system
Building load central cooling (kWh) | 8925.4402
Pumps cooling load (kWh)
Pipes thermal losses (kWh) | 0
Thermal energy storage losses (kWh)
Produced cooling (kWh) | 12023.2391
Parasitic energy heating
Pumps (kWh) | 919.5601
Parasitic energy cooling
Pumps (kWh)
Boilers
Usefull heat (kWh) | 16843.329
Fuel consumption (kWh) | 18442.2139
Efficiency (%) | 91.33%
Pellet boilers
Usefull heat (kWh) | 0
Fuel consumption (kWh) | 0
Efficiency (%) | #DIV/0!
CHPs
Usefull heat (kWh) | 1644.7908
Electricity production (kWh) | 950.7391
Fuel consumption (kWh) | 2851.212
Thermal efficiency (%) | 57.69%
Electrical efficiency (%) | 33.35%
Operating time (h) | 45.7828
Number of start/stops (#) | 2
Average continuous operating time (h) | 22.8914
HPs
Condenser heat flow (kWh) | 19688.1912
Evaporator heat flow (kWh) | 14635.8564
Electricity consumption (kWh) | 5052.3794
SCOP (-) | 3.8968
Operating time (h) | 83.9241
Number of start/stops (#) | 222
Gas absorption HPs
Condenser heat flow (kWh) | 0
Fuel consumption (kWh) | 0
SCOP (-) | #DIV/0!
Operating time (h) | 0
Number of start/stops (#) | 0
Solar collectors
Usefull heat (kWh) | 206.2893
HP/Chillers
Condenser heat flow (kWh) | 13087.383
Evaporator heat flow (kWh) | 9365.3786
Electricity consumption (kWh) | 3722.0099
SCOP (-) | 3.5162
SEER (-) | 2.5162
Operating time (h) | 37.4996
Number of start/stops (#) | 46
Chillers
Condenser heat flow (kWh) | 1846.5211
Evaporator heat flow (kWh) | 2657.8604
Electricity consumption (kWh) | 1833.9722
SEER (-) | 1.4492
Cooling towers
Usefull cooling (kWh) | 0.00013134
Ice storage tanks
Usefull cooling (kWh) | 0
Primary energy for storage (kWh) | 0
Thermal energy for storage (kWh) | 0
Delivered heating contributions
Boilers produced heat contribution (kWh) | 61.64%
Pellet boilers produced heat contribution (kWh) | 0%
CHPs produced heat contribution (kWh) | 6.02%
HPs produced heat contribution (kWh) | 72.05%
Gas absorption HPs produced heat contribution (kWh) | 0%
Solar collectors produced heat contribution (kWh) | 0.755%
HP/Chillers produced heat contribution (kWh) | 47.9%
Delivered cooling contributions
HP/Chillers produced cooling contribution (kWh) | 77.89%
Chillers produced cooling contribution (kWh) | 22.11%
Cooling towers produced cooling contribution (kWh) | 1.092e-06%
Ice storage tanks produced cooling contribution (kWh) | 0%
Energy analysis
Gas consumption (kWh) | 21293.4259
Electricity consumption (kWh) | 11527.9216
Electricity production (kWh) | 950.7391
Total energy consumption (kWh) | 32821.3475
Primary energy consumption (kWh) | 50113.23
System efficiency (%) | 145.2%
PER (%) | 95.09%
RPES (%) | 3.234%
Energy cost analysis
Gas consumption cost (€) | 851.737
Electricity consumption cost (€) | 1268.0714
Electricity production reduced cost (€) | 104.5813
Total energy cost (€) | 2015.2271
CO2 analysis
CO2 emission (ton) | 8014.9756
Parameters
Energy price gas (€/kWh) | 0.04
Energy price electricity (€/kWh) | 0.11
COP economic switching point (€/€) | 2.475
CO2 emission factor gas (kg/kWh) | 0.21
CO2 emission factor electricity (kg/kWh) | 0.335
COP ecologic switching point (kg/kg) | 1.4357
Power grid efficiency (%) | 40%