## Hysopt incl CIBSE CP1
This file describes the pressure profile for different pipe types
Sheet 1 : the name of this sheet will be used as the name of the profiles
Sheet 2 : maximal pressure loss (in Pa) and/or maximal velocity (in m/s)
Sheet 3 : target pressure loss (in Pa)
Both velocity and pressure loss serve as 'hard' filtering criteria. A pipe diameter is NEVER
selected when the pressure loss is larger than the maximum, or the velocity is larger than the
maximum velocity.
When target pressure losses are supplied, the pipe diameter is selected from the set of diameters
which are allowed (by the above criteria), and which has the smallest deviation from the
target pressure loss.
Do not change the order of these sheets!

## Max pressure loss & Veloc per m
PipeType | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.welded | steel.pipe.seamless | steel.pipe.seamless | steel.pipe.seamless | steel.pipe.seamless | steel.pipe.seamless | steel.pipe.seamless | steel.pipe.seamless | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | copper.pipe | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | steel.pipe.precision | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | plastic.or.multilayer | epoxy.pipe | epoxy.pipe | epoxy.pipe | epoxy.pipe | epoxy.pipe | epoxy.pipe | epoxy.pipe | epoxy.pipe | epoxy.pipe | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | hdpe.100.sdr.11 | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | steel.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE
Name | DN 15 | DN 20 | DN 25 | DN 32 | DN 40 | DN 50 | DN 65 | DN 80 | DN 100 | DN 125 | DN 150 | DN 200 | DN 250 | DN 300 | DN 350 | DN 400 | DN 450 | DN 500 | DN 600 | DN 10 | DN 15 | DN 20 | DN 25 | DN 32 | DN 40 | DN 50 | 12x1 | 15x1 | 18x1 | 22x1 | 28x1.5 | 35x1.5 | 42x1.5 | 54x2 | 64x2 | 76.1x2 | 88.9x2 | 108x2.5 | 12x1 | 15x1 | 18x1 | 22x1.5 | 28x1.5 | 35x1.5 | 42x1.5 | 54x1.5 | 64x2 | 76.1x2 | 88.9x2 | 108x2 | 14x2 | 16x2 | 18x2 | 20x2 | 26x3 | 32x3 | 40x3.5 | 50x4 | 63x4.5 | 75x7 | DN 50 | DN 80 | DN 100 | DN 150 | DN 200 | DN 250 | DN 300 | DN 350 | DN 400 | DN 20 | DN 25 | DN 32 | DN 40 | DN 50 | DN 63 | DN 75 | DN 90 | DN 110 | DN 125 | DN 140 | DN 160 | DN 180 | DN 200 | DN 225 | DN 250 | DN 280 | DN 315 | DN 355 | DN 400 | DN 450 | DN 500 | DN 25 | DN 32 | DN 40 | DN 50 | DN 65 | DN 80 | DN 100 | DN 125 | DN 150 | DN 200 | DN 250 | DN 300 | DN 25 | DN 32 | DN 40 | DN 50 | DN 63 | DN 75 | DN 90 | DN 110 | DN 125 | DN 140 | DN 160
maximalPressureLossPerMeter (Pa) | 240 | 160 | 150 | 150 | 150 | 150 | 130 | 110 | 80 | 60 | 50 | 38 | 26 | 20 | 15 | 15 | 15 | 15 | 15 | 325 | 240 | 160 | 150 | 150 | 150 | 150 | 350 | 240 | 180 | 150 | 110 | 85 | 60 | 50 | 50 | 50 | 50 | 50 | 325 | 280 | 200 | 170 | 150 | 150 | 150 | 150 | 150 | 130 | 110 | 80 | 475 | 290 | 240 | 200 | 155 | 135 | 83 | 61 | 45 | 37 | 150 | 110 | 80 | 50 | 38 | 26 | 20 | 15 | 15 | 350 | 350 | 350 | 300 | 275 | 200 | 180 | 140 | 110 | 100 | 90 | 80 | 60 | 65 | 55 | 50 | 45 | 40 | 35 | 30 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
maximalVelocity (m/s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 1.17 | 1.3 | 1.3 | 1.69 | 1.82 | 1.95 | 2.34 | 2.6 | 3.12 | 3.12 | 3.25 | 1.2 | 1.2 | 1.32 | 1.56 | 1.68 | 1.8 | 1.86 | 1.92 | 2.04 | 2.16 | 2.28

## Target pressure loss per m
PipeType | steel.pipe.welded | steel.pipe.seamless | copper.pipe | steel.pipe.precision | plastic.or.multilayer | epoxy.pipe | hdpe.100.sdr.11 | steel.pipe.external.CP1.CIBSE | PEX.pipe.external.CP1.CIBSE
targetPressureLossPerMeter (Pa) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0